[image: image1.jpg]5023 HAZEL JONES ROAD, BOSSIER CITY, LA 71111
800.747.8954

800.877.8746 FAX
SALES@GORDONDATACENTERS.COM
GORDONDATACENTERS.COM

DATA CENTER PRODUCTS DIVISION AN EMPLOYEE OWNED COMPANY




STRUCTURAL ScrewSlot DATA CENTER CEILING GRID 
SPECIFICATION SECTION 09 54 00
PART 1:  GENERAL

1.1 RELATED DOCUMENTS

 A.
Drawings, General and Supplementary Conditions and Division 1 apply to Work specified in this section.

1.2 DESCRIPTION OF WORK

A. Furnish and install extruded aluminum suspended Structural ScrewSlot Data Center ceiling grid system as manufactured by Gordon Data Center Products and as indicated on drawings, including notes and details.

1.3 WORK INCLUDED

A. Work on this Section includes the installation of the cleanroom ceiling grid system including but not necessarily limited to the following:

1. Aluminum ceiling grid:  As specified in this Section.

2. Threaded rod and turnbuckle:  As specified in this Section.

1.4 RELATED WORK

A. Intermediate steel framing:  As specified in Division 5.

B. Lay-in and/or surface mounted light fixtures:  As specified in division 16

1.5 PERFORMANCE

A. Completed ceiling system shall be capable of providing direct suspension of cable trays and other utilities as required and indicated for area installed.
PART 2:  PRODUCT

2.1 ACCEPTABLE MANUFACTURER

A. Gordon, Inc. “DG 1538 ScrewSlot Data Center Ceiling Grid”

2.2 CEILING SUPPORT MATERIALS AND SYSTEMS

A. DG-1538 ScrewSlot DATA CENTER CEILING GRID AND SUSPENSION 

1. DG-1538 ScrewSlot Data Center Grid – The grid system shall be manufactured of extruded aluminum alloy 6063, temper T5 with a 204-R1 etched and clear anodized finish. Grid profile shall have a 1.5-inch wide face with a continuous integral thread boss within the web for attachment of intersection connectors at any point along the top of the grid members, and to facilitate ease of field installation.  
2. 12’ Main Runners and 4’ (nominal length) Cross Tees shall have a continuous 3/8-16 ScrewSlot thread boss feature  to allow direct attachment of cable trays, utility racks, partition wall system head tracks, surface-mounted lighting fixtures, softwall curtain tracks or other accessories. 

3. Optional Gasket – To minimize air leaks, a 3/32-inch thick x 3/8-inch wide closed cell polyethylene gasket tape shall be provided.  The gaskets shall be factory-applied, with precision cut ends, extended on grid members to ensure an airtight seal at all intersections.  

4. Suspension system  

a. Model G-38 grid connectors – Heavy duty zinc alloy casting connectors shall be used at grid intersections and to suspend the grid system via 3/8-16 threaded rods.  ¼-20 phillips drive button head cap screws are used to fasten the connectors to the extruded aluminum grid members.  

b. 3/8-16 Threaded Starter Rod and Turnbuckle– ASTM rated RH/LH, 8” long, zinc plated, 3/8-16 threaded rod and 6” body zinc plated steel turnbuckle spaced at 48” centers along the main runners, for a 4’ x 4’ nominal suspension from building structure.
5. Structural

a.
Ceiling system with 4’ x 4’ suspension, shall be capable of supporting a 
fully populated ceiling grid, including blank panels, HVAC supply and 
return registers, and light fixtures, plus directly supporting cable trays, 
utility racks, and other accessories.
b.
The ceiling system shall be capable of supporting uniform loads to 21 lbs per square foot, dynamic.  Maximum concentrated load:  336 lbs, static 
 
PART 3:  INSTALLATION

3.1 DS GRID INSTALLATION

A. Wall Angle Installation

1. Position wall angle at proper ceiling height on center of wall using a laser leveling device and attach with fasteners appropriate for existing wall type.  Continue installing toward the corners and then around the room until complete.  Corner can be field cut with a power miter saw using a carbide tipped blade.  All joints must fit tight with no gaps.

2. Optional perimeter main tee installation:  Perimeter main tee extrusions shall be suspended from structure at the proper ceiling height and using a laser leveling device, beginning at the center of the room.   Continue installing toward the corners and then around the room until complete.  Corner can be field cut with a power miter saw using a carbide tipped blade.  All joints must fit tight with no gaps.  Secure partition wall head tracks to the ScrewSlot perimeter main tees.
B. Grid Installation

1. Position main tees at 48” or 48 ½”, or as required, perpendicular to wall angle taking care to align notches on main tee with notches on wall angle.  Attach threaded rod previously hung by others from steel structure to turnbuckle and rod attached to connectors on grid.

2. Level entire ceiling to within 0.10” overall and/or 0.06” in any 10’ length.

3. Brace grid for seismic conditions when required by local code.  Install in accordance with UBC Standard No.47.18 and ICBO No 1461 for aluminum grid.

4. Peel backing off overhanging ends on gasket tapes and carefully affix to the grid member across the intersection seam and compressing into the gasket tape on the main runner.  A tight fitting gasket intersection will assure the most airtight seal.

3.2 INSTALLATION GENERAL

 A.
Coordinate all work with other trades to be performed in or on ceiling system including light fixtures, HVAC equipment, sprinkler systems and wall partition systems.
Section 09 54 00
Page 3
Rev 09/11

